FAA Response to Honeywell RFI #3.

1.      There is no power shown for the VESDA system in room B101C.  Please provide the circuit location for powering this panel.

EPP-1, breaker #17.  EEP-1 is located in the Control Wing Basement Equipment Room B120

2.      Please provide the model number of the desired VESDA system.

Vesda VLP LaserPlus

3.      28 31 00 – Page 6 – 1.6 System Description Item K.

a.       Alarm Silencing – When the alarm silence button is activated at the FACP, the audible notification appliance shall stop, while the visible device continue.  If a subsequent alarm occurs, the audible device shall re-activate.

b.      The Honeywell existing system does not currently have this functionality.

c.       We will need to add a power supply and additional wire to all horn/strobes in the basement of Admin Wing and Control Wing.

d.      This will require a rewiring of all the horn/strobes in the basement B120 N/S, B134, Host Room, B101C and all the administration basement wing and the device replacement.

e.       Please confirm this is desired.

Currently the existing system in the CWB has a combined silence feature for the Horn and Strobe.  This feature will remain the same as existing conditions for the new work in B101 and other applicable areas in the CWB.